## Slide 1: Pressure Drop in Parallel Plates Heat Exchanger

## Slide 2: Introduction
It is essential to calculate pressure drop in a heat exchanger as it helps us in knowing the amount of power required to blow the fluid across the heat exchanger.
Accordingly, we can plan what power of fan we require to blow the air in our case and whether our design of heat exchanger is feasible of not. Our design will be not feasible if the pressure drop is too large and our fan is unable to overcome the pressure drop.
Pressure drop in the heat exchanger can be because of many reasons such as due to friction, gravity, fluid acceleration etc.
In our case, the major cause of pressure drop is friction. Since our heat exchanger is horizontal and the fluid is not accelerating, we can safely neglect the pressure drop due to the other factors.

## Slide 3: Objective
As the pressure drop is very important to consider, our aim is to calculate its value using the dimensional parameters of the parallel plates heat exchanger.
The dimensional parameters of the heat exchanger includes its length(along the flow of the fluid), width, spacing between the plates and number of plates.

## Slide 4: Dimensional Parameters

## Slide 5: Calculation of Pressure Drop
First, we calculate the velocity of the air flowing through heat exchanger using its mass flow rate, density and dimensional parameters of the heat exchanger.
Next, we calculate the dynamic viscosity of the air flowing.
We calculate the reynold’s number of the air.
Further, we apply Blasius Correlation to calculate the Darcy friction factor, f.
Finally, we apply Darcy-Weisbach equation to calculate the pressure drop in the heat exchanger.

## Slide 6: Mathematical Model
Calculation of Velocity: V = ṁ/(ρ*N*h*W), where N is number of plates and ρ is density of air.
Calculation of Dynamic Viscosity:
(Sutherland Equation)
where T is temperature of air, b and S are constants whose values are
and .
3. Calculation of Reynolds Number:

## Slide 7
Mathematical Model
(contd.)
Calculation of Darcy friction factor:
f = 0.316/Re 1/4. (Blasius Correlation)
Calculation of Pressure Drop:
Δp = f (L / Dh) (ρ V2 / 2) (Darcy-Weisbach Equation)
where Dh is hydraulic diameter.

## Slide 8: Sample Calculation
For a heat exchanger with dimensions: L = 0.2 m, W = 0.6 m, N = 100 and h = 2.7 mm, and mass flow rate, ṁ = 0.5 kg/s, (applying the mentioned equations) we calculate :
Velocity of air, V = 2.5 m/s
Dynamic Viscosity, µ = 1.846 * 10-5 Pa-s.
Reynolds Number, Re = 1,30,020.
Darcy friction factor, f = 0.01664.
Pressure drop, Δp = 31.06 Pa.

## Slide 9
Thank You!